## Parameters
Set | Component | var | Description | Value | Units
J | PV | CFInv | Investment Cost Factor | 1910 | $/kW
J | ICE | CFInv | Investment Cost Factor | 600 | $/kW
J | DSL | CFInv | Investment Cost Factor | 1013 | $/kW
J | MT | CFInv | Investment Cost Factor | 897 | $/kW
S | BESS | CFInv | Investment Cost Factor | 580;100 | ($/kWh);($/kW)
S | TESS | CFInv | Investment Cost Factor | 75;20 | ($/kWh);($/kW)
N | HAC | CFInv | Investment Cost Factor | 1706.0722 | $/kW
N | EC | CFInv | Investment Cost Factor | 1349.999 | $/kW
J | ICE | CF | Fuel Price | 1 | $/m3
J | MT | CF | Fuel Price | 0.85 | $/m3
J | PV | CF | Fuel Price | 0 | NA
J | DSL | CF | Fuel Price | 0.7 | $/L
J | PV | Pmin | Minimum operative limit | 0 | p.u.
J | ICE | Pmin | Minimum operative limit | 0.3 | p.u.
J | DSL | Pmin | Minimum operative limit | 0.3 | p.u.
J | MT | Pmin | Minimum operative limit | 0.3 | p.u.
J | PV | PjRampDown | Down-ramp Limit | 1 | p.u.
J | ICE | PjRampDown | Down-ramp Limit | 0.9 | p.u.
J | DSL | PjRampDown | Down-ramp Limit | 0.7 | p.u.
J | MT | PjRampDown | Down-ramp Limit | 0.7 | p.u.
J | PV | PjRampUp | Up-Ramp limit | 1 | p.u.
J | ICE | PjRampUp | Up-Ramp limit | 0.9 | p.u.
J | DSL | PjRampUp | Up-Ramp limit | 0.7 | p.u.
J | MT | PjRampUp | Up-Ramp limit | 0.7 | p.u.
J | PV | phij | Heat-recovery factor | 0 | kW/kW
J | ICE | phij | Heat-recovery factor | 0.2 | kW/kW
J | DSL | phij | Heat-recovery factor | 0 | kW/kW
J | MT | phij | Heat-recovery factor | 0.3 | kW/kW
N | HAC | Qmin | Minimum operative limit | 0 | kW
N | EC | Qmin | Minimum operative limit | 0 | kW
S | BESS | deltasd | Self-dicharge factor | 0.00041667 | kWh/h
S | TESS | deltasd | Self-dicharge factor | 6e-06 | kWh/h
N | HAC | COP | Coefficient of performance | 0.9 | NA
N | EC | COP | Coefficient of performance | 6.5 | NA
S | TESS | SOCmin | Minimum allowable SOC | 0.3 | NA
S | BESS | SOCmin | Minimum allowable SOC | 0.3 | NA
S | TESS | SOCmax | Maximum allowable SOC | 0.95 | NA
S | BESS | SOCmax | Maximum allowable SOC | 0.95 | NA
S | BESS | etart | Round-trip efficiency | 0.9 | NA
S | TESS | etart | Round-trip efficiency | 0.8 | NA
P | NA | Y | Project's lifespan | 15 | years
NA | NA | d | Discount rate | 6% | %
NA | NA | Ud | Demand error distribution mean | 0% | NA
NA | NA | Sd | Demand standard deviation for error distribution | 2% | NA
NA | NA | Us | Error mean of solar production forecast | 0% | NA
NA | NA | Ss | Standard deviation of demand error | 10% | NA
NA | NA | npos | Positive violation probability for spinning reserve | 5% | %
NA | NA | nneg | Negative violation probability for spinning reserve | 5% | %